Installation & Operation Manual

Model TDS-2 Telemetry Interface Unit

FirstPoint Energy Corporation

1800 NW 169th Ave, Suite B-100

Beaverton, OR 97006

Phone:	503-425-5152

FAX:	503-425-5010

Email:	pcarmin@firstpoint.com

Website:  www.firstpoint.com

Written 	03/02/10

Revision	1.0

TeldataManager ™

The software described in this manual is furnished under a license agreement and may be used only in accordance with the terms of that agreement.

Copyright Notice

Copyright© 2000 Teldata, Inc. All Rights Reserved.

Trademarks

TeldataManager® is a registered trademark of FirstPoint Energy Corporation.

Windows95™ & NT is a registered trademark of Microsoft® Corporation. Other product names mentioned in this manual may be a trademark or registered trademarks of their respective companies and are so acknowledged.

Technical Support

Contact FirstPoint’s Customer Support Service at:

Voice	888.422.8484

Fax	503.425.5010

FirstPoint Energy Corporation

1800 NW 169th Ave, Suite B-100

Beaverton, OR 97006

E-mail	pcarmin@firstpoint.com

Industry Canada (IC) Notice

The Industry Canada (IC) label identifies certified equipment. Certified equipment meets telecommunications network protective, operational, and safety requirements as prescribed in the appropriate Terminal Equipment Technical Requirements document(s). The department does not guarantee the equipment will operate to the user’s satisfaction.

Before installing this equipment, be sure that it is permissible to connect to the local telecommunications facility. Install the equipment using an acceptable connection method. The customer should be aware that compliance with the above conditions might not prevent degradation of service in some situations.

A designated representative should coordinate repairs to certified equipment. Repairs or alterations made by a user to this equipment, may give the telephone communications company cause to request the user to disconnect the equipment.

Users should ensure for their own protection that the electrical ground connections of the power utility, telephone lines, and internal metallic water pipe system, if present, are connected. This precaution may be particularly important in rural areas.

Caution: Users should not attempt to make such connections themselves, but should contact the appropriate electric inspection authority.

NOTE: The Ringer Equivalence Number (REN) assigned to each terminal device provides an indication of the maximum number of terminals allowed to be connected to a telephone interface. The termination of an interface may consist of any combination of devices subject only to the requirement that the sum of the Ringer Equivalence Number of all the devices does not exceed 5.

# REN: 0.1

Contents

Overview: The TDS-2 TIU	3

Pulse Accumulation in the TDS-2	3

Pulse Accumulator Initialization	4

Demand Window Initialization	4

Field Installation: TDS-2 TIU	5

Placement	5

Electrical Connections	6

Ports	6

TDS-2 Board Layout	7

Connecting to Encoders	8

Connecting to Pulse Initiators	8

RS-1 Installation to TDS-2	9

Telephone Line operation	10

Field Programming the TDS-2	11

Basic Programming	13

GO & SET Commands	15

Set Commands	16

Go Commands	17

Error Messages	18

Manual Call Initiation without a Programming Terminal	19

TDS-2 Pulse Accumulators	21

Changing Pulse Values	22

Field Correlation of Pulse Totals to Meter Faceplate Reading	23

Using the Field Programmer to Verify  Readings	26

Replacing a TDS-2 in the Field	26

Power Fail Log and Alarm	28

Port Tampers	29

Setting a delay before dialing	30

Appendix A:	30

Field Pro - Operations Manual	30

TIU Programming Terminal	30

Appendix B: Factory Defaults	34

Appendix C: Tamper Register Matrix	35

Appendix D: Trouble Shooting	36

Appendix E: Tamper Connection for Water Meter	36

Appendix F: Port Configuration Registers	37

Appendix G: Power Fail Programming Matrix	43

Appendix H: Host to call matrix	44

Appendix I: TIU Report Header	45

Glossary	47

Advanced Programming.	49

Clearing Logged Memory	49

Assigning Host To Call Vectors	49

Register 	Register Defined	49

Checking the Host To Call Vector Assignment	50

Changing Host To Call Vector Assignment	50

Multi-Host Telephone Number Programming	50

Dynamic Off Hook Detection	51

# Overview: The TDS-2 TIU

The TDS-2 is a battery-powered device with an AC power option.  The AC power option is necessary only to enable real time power fail reporting.

The TDS-2 will log interval data down to a 10-minute resolution from 2 meters when they are directly wired to the meter ports and no RF receiver is present.

The meter connectors are identified as METER1 and METER2 and can accept input from 2-wire Form A pulse initiators or 3-wire electronic encoders.

When the TDS-2 is equipped with an RF receiver board, METER1 channel continues to function as a direct wire port.  However, METER2 channel now becomes RF channels 1, 2 & 3, with channels 2 & 3 fixed at daily data logging at midnight of each day.

METER1 (Port1)

(5-minute interval DATA storage MODE)

When the METER1 channel is set to log 5-minute interval data the METER2 (even if hardwired) channel is limited to midnight data logging only.

The RF functionality is unaffected by this.

In this mode all of the non-midnight interval data storage capacity of the TDS-2 is allocated to Meter Port 1.

In this mode the 5-minute interval data storage capacity of the TDS-2 before memory wrap around is 49.6 days.

Pulse Accumulation in the TDS-2

The TDS-2 accumulates and stores raw pulses from each meter. The TeldataManager software in the host computer converts these pulses to engineering (consumption) units. The conversion multiplies the transmitted TDS-2 pulse totals by a pulse value on each meter type constant. This value is entered into the TeldataManager database for each meter port on the TDS-2. You can initialize the TDS-2 pulse accumulators to match existing meter face reads utilizing a FieldPro terminal, laptop, or the Host computers via telephone line.

Pulse Accumulator Initialization

Once the TeldataManager host software has been programmed to allow recognition of a new TDS-2, the system can load the initial pulse accumulator pulse total over the telephone line. The host must set the init registers to allow activation of the GO1 command on call-in. Upon recognition of the GO1 command, the pulse accumulator is reset to correspond to the set registers.

In this procedure, the installer uses a field programmer to enter the current faceplate reading into one or more TDS-2 “SET” registers. The installer then directs the TDS-2 to call the host computer, which will calculate and load the corresponding pulse accumulator with the equivalent pulse total.

Demand Window Initialization

The TDS-2 has the capability to be programmed to only respond to an incoming demand call within a specified window of hours.

The register used to set this function is the E26 register.

Example:  E2600-00 = 24 hour response to an 			  incoming demand

E2602-03 = Responds only between two 			  and three AM.

E2622-23 = Responds only between ten 			  and eleven PM.

The TDS-2 can be set to call the central computer in response to a one ring demand or to auto-answer an incoming call.

The window allows several TDS-2s to be placed on a single phone line and still allows each unit to be capable of responding to a demand call on an individual basis.

This function also enhances the TDS-2s capability to be demand rung without interfering with the resident in a shared line situation.

# Field Installation: TDS-2 TIU

## Placement

Determine the physical placement of the TDS-2 TIU at the installation site according to the following factors:

###### Minimizing cable-run distance

Telephone line cable lengths are non-critical.

Susceptibility to noise on meter data cable increases with length (500’ maximum).

###### Environmental considerations

Avoid mounting the TIU directly under a roof “drip-line” if possible.

Mount TIU at least 18” above ground level to help avoid water splashing on the wire entry ducts.

If possible, mount the unit at 5’ to minimize insect intrusion.

Mount the TIU so as to minimize exposure to direct sunlight.

If you use conduit with this product, it must be rated for outdoor use.

CAUTION: Danger of explosion if battery is incorrectly replaced. Replace only with the same or equivalent type recommended by the manufacturer. Dispose of used batteries according to the manufacturer’s instructions.

### Electrical Connections

Electrical connections to the TIU should follow the sequence outlined below:

- Connect the meters to the ports.

- If using the AC power option connect the AC Power.

- Connect the program terminal and program the unit.

- Connect the phone line.

# Ports

Each meter port contains 3 screw terminals labeled C, G, and D. Use all three terminals to read encoders. Use only terminals G and D to read pulse initiators.

C= Clock: Output signal used to power or clock an electronic encoder.

G= Signal Ground (pulse -): References for encoders or negative side of pulse input.

D = Data (pulse +): Inputs to the TIU from encoder.

### TDS-2 Board Layout

### Connecting to Encoders

Connection to encoding meters varies with manufacturer. Some commonly encountered types are listed below:

| Meter Type | (C) Clock | (G) Ground | (D) Data |
| --- | --- | --- | --- |
| Sensus ECR (Gas & Water) Landis & Gyr | R | B | G |
| Sangamo T2000 Schlumberger ARBIII-V | B | G | R |
| Kent Scancoder | G | B | R |

### Connecting to Pulse Initiators

Pulse Initiators include solid-state switches, metallic contact switches, and voltage pulses.

Pulse output meters connect to the G and D terminals on each meter port (G = negative, D = positive). The C terminal should be left floating.

#### Powering Options

- TDS-2, 12 Vac, .48VA (40ma) 50-60 Hz.

- 115 and 230 Vac power modules are also available for use with the TDS-2. (Commercial enclosure required)

- The RS-1 (electric meter retrofit unit) can also supply power to this model, as described on the next page.

### RS-1 Installation to TDS-2

#### Meter Port Connections

| TIU Meter Port | RS-1 Output Cable |
| --- | --- |
| C | No Connection |
| G | White (-) |
| D | Red (+) |
| 12-volt AC input | Black AC output |
| 12-volt AC input | Black AC output |

The Teldata Model RS-1 contains a step-down transformer powered from the electric meter’s line-side input Buss. The two black conductors in the RS-1 output cable can supply 12VAC to the TDS-2.

#### TDS-2 (Residential installation)

The TDS-2 residential enclosure is a wall- or pipe-mount enclosure designed with a sliding cover and two wire ducts with grommets.

The residential enclosure does not provide mounting space for the 115Vac or 230Vac power modules.

The RS-1 (residential electric meter retrofit device) can provide the optional 12VAC and is capable of supplying 40ma maximum.

A 115vac to 12VAC wall mount power supply can also be used to supply the TDS-2 with the optional 12VAC.

### Connection of power to the TDS-2 is made to the two-position terminal block on the left side of the circuit board labeled 12V AC .

### Telephone Line operation

The TDS-2 is compatible with, Key and PBX system analog phone lines and standard, public switched telephone network, POTS lines.

The TDS-2 automatically adjusts itself for operation on any analog phone line with a DC voltage level of 20V or higher.

The TDS-2 requires no external or internal operator intervention to make these phone line adjustments they are fully automated within the TDS-2.

The TDS-2 also automatically adjusts its internal dynamic and static off-hook sensing capabilities for operation on phone lines in this range.

The TDS-2 will not work on the digital side of office PBX or Key systems.

The telephone line connection is made to the two-position terminal block located at the bottom left and is marked Phone Line.

The telephone line connection is not polarity sensitive.

# Field Programming the TDS-2

#### Data Entry Requirements

The Teldata TDS-2 Telemetry Interface Unit (TIU) must be programmed with an ID # and phone # (see Appendix A for programming instructions).

Note: The @ character used in the following pages is a non-display character when entered as a prefix to a command. It does not print.

- Enter TIU Identification

Enter an alpha or numeric string of characters without spaces (use dashes or other character to delimit between words) unique to the particular TIU. This unique character string must be entered in TeldataManager for recognition of the TDS-2 when it calls in. You may enter a maximum of 31 characters.

- Enter Host Telephone Number

Enter the telephone number of the host computer modem. You may use a maximum of 21 characters.

Variations

Pulse Dialing: If you enter a P before the telephone number, the TDS-2 will use pulse dialing.

Inter-digit Pauses:

A P entered between digits will cause inter-digit pauses in dialing of one second each.

Extend TDS-2 Timeout: You can extend the TDS-2’s wait time for an answering modem by adding Ps after the telephone number.

TIUs are designed to stay on the line for up to 23 seconds. If you need to extend this time period, you can enter a P after the telephone number, telling the TDS-2 to pause and keeping the telephone off the hook. Each P entered after the telephone number extends the wait time 1 second. This method is particularly useful when installing a unit behind cellular and PBX interfaces in which you must dial an additional number (such as 9) or access code to make an outside call.

Note: Items #3 and #4 are preset with factory defaults but may be reset.

- Ring # (Number)

Establish the number of rings that will trigger the 	TDS-2 to make an unscheduled inbound call or an 	auto-answer sequence (depending on whether the 	auto-answer mode is selected in Step 4 below). 	You must enter the ring count as two digits from 	01 to 63.

4.   Auto-Answer Mode

The TDS-2 may be set to automatically answer 	the phone line depending upon the number of rings 	programmed into the Ring #.   To enable or disable 	the feature see below.

Auto Answer = (1=Yes, 0=NO)

### Basic Programming

Programming involves connection of a suitable ASCII terminal to the 9-pin header labeled PROGRAM in the upper right corner of the TDS-2 circuit board. If the terminal is set up correctly, when you switch on the terminal and press Enter, an asterisk (*) prompt will appear on the screen.

(For programmer set-up, see Appendix A.)

All programming begins at the asterisk (*) prompt. You can return to the * prompt at any time during programming by pushing the F1 key. To backspace during programming, hit the F2 key.

#### Basic Programming Using the PRO Command

The PRO command programs the unit ID, call-in phone number, mode of operation, and the ring count for alert.

The transaction is as follows:

*PRO

ID# = 0

>310_south_street (Enter)	this is the new ID

HOST1 PHONE# = 0123456789

>3773456 (Enter)	this is the new telephone number

RING # = 10

>(Enter)		retains current ring count

AUTO ANSWER = 0 (disabled)

>(Enter)		retains current status

*			ready for new command

To check if programming was successful, re-enter the PRO command and enter through the fields. If any changes are necessary, enter them at the > sign after the field.

The * prompt signals the conclusion of the PRO entry sequence. To review the entries made, type PRO again in response to the * prompt and press Enter key at the > prompt after each item is displayed.

- Synchronize Initial Meter Reads (Pulse Initiating Meters only)

Synchronize TDS-2 pulse accumulators to the meter’s faceplate reading at the time of installation. (See the section below SET and GO Commands for a complete description of this process.)

- Setting the Clock (Manual procedure)

When the TIU is shipped its real time clock will not be set to local time. Standard installation practice calls for the central computer to set the clock automatically when the TIU makes its first call; however, some situations may require you to set the clock manually to local time.

See the next page for instructions:

Setting the clock manually:

To see the current clock setting type exactly as follows:

- (shift)+@T(<enter>): displays the clock

- To change the time: (shift)+@THH:MM:SS

- To see the current date type: (shift)+@D<enter>

- To change the date: <shift)+@DMM:DD:YY<enter>

# GO & SET Commands

The GO1 and GO2 & SET commands prompt the software to make the calculations that will synchronize the TDS-2 pulse accumulation register(s) with the meter face relieving the installer of the task.

### Set Commands

- Using the SET1 and SET2 commands, enter an existing meter’s faceplate reading. Using SET1 provides the data necessary for initialization of TDS-2 Meter Port #1’s pulse Totalizer. SET2 allows proper initialization of Meter Port #2.

Example:

Enter a face read into Meter Port #1’s set register to correspond to a faceplate reading of 01207.

TRANSACTION		DESCRIPTION

*SET1

READ = 00000000	Displays any previous data.

>01207 (Enter)		Enter current reading.

When tracking delivered KWH, you must multiply the face read by the meter multiplier and enter the product of the two into the set register.

(The SET registers accept up to an 8-digit entry.)

- To complete initialization once the SET registers are loaded, instruct the TDS-2 to call the TeldataManager software utilizing a GO1 command (see next page).

Note: The host computer only uses the set register “face read” data to calculate the equivalent pulse total. It has no other use or function in the TDS-2 or the system.

If the TDS-2 is unable to make the call, error messages will appear on the display. (See the following page for a breakdown of these messages.)

If communication with the Host is established, the message CALL OK will appear.

Note: This message means only that communication was established; you would receive this message even with an erroneous TIU ID.

Disconnect the terminal from the TDS-2.

During the first call, the TeldataManager software completes any remaining TDS-2 programming tasks, including the auto-initialization of the Meter Port pulse accumulator (if you have used the SET command entry procedure).

### Go Commands

(Used to initiate TDS-2 calls from the field)

The TDS-2 stores four phone numbers (E01, E03, E05, and E07). The “GO” commands allow the installer to select the phone number or ‘HOST’ to be dialed by typing in GO1 (E01), GO2 (E03), GO3 (E05) or GO4 (E07).

The GO command sets a flag in the data stream it sends to the host computer. When the software receives this flag the system checks for initialization flags in the database to determine whether it should utilize the SET register (meter face read) information in the TDS-2 to calculate an equivalent pulse total and reprogram the pulse accumulation register with the new total.

#### Go Command Used in a Single-host System

When the TIU is calling only one host computer, use the GO1 command. The GO1 command uses the phone number entered with the PRO command. In a single-host system, all data collected from any meter connected to the TDS-2 will be reported to that computer.

#### GO Command Used in a Multi-host System

In a multi-host system, the GO command determines the host to call (i.e.: GO1 - Host1). The host called is able to access only the data defined by the software for that host.

After entering the command GO1 at the * prompt with the field programming terminal:

If you have a good connection to the telephone line and the line is not currently in use, the light–emitting-diode (LED) located on the bottom right of the TDS-2 circuit board will illuminate. There may be a few seconds delay while the TDS-2 verifies the telephone line is clear. This LED (labeled LED1) will remain illuminated for the duration of the call.

## Error Messages

| Error Messages and Conditions | Action |
| --- | --- |
| ERROR 0 = Line not available |  |
| >Telephone line not connected. | Verify that the DC telephone line voltage at telephone connection to TDS-2 is the correct level for the type of phone system |
| >Telephone line in use | Verify no incoming rings and that resident is not using line. |
| ERROR 1 = Host modem won’t answer |  |
| >Wrong phone # in TIU | Check TIU programming |
| >Host computer problem | Call Host computer # with a telephone set and verify answer & reception of modem tone |
| ERROR 2 = Host computer modem answers but fails in Handshake |  |
| >Host Computer Problem | Verify other TIUs are communicating properly |
| >Defective TIU | Replace TIU |
| ERROR 5 = Communication interrupted |  |
| >Customer went off hook | Monitor line availability with Butt in set or voltmeter. When available try again. |
| >Lost communication with the Host computer during communications session | Check database to insure proper record entry to support TDS-2. Insure Ticomm version supports TDS-2 TIUs. |

## Manual Call Initiation without a Programming Terminal

You can trigger the TDS-2 to call in to the Host computer using a metallic object such as a screwdriver or key to short the two pins labeled CALL START (located to the left of the Program Header). TICOMM treats this method of call initiation as a “start pin” call and, consequently, TeldataManager will not support SET register pulse accumulator initialization.

### TDS-2 Pulse Accumulators

#### Accessing Pulse Values

Each of the two-meter ports on the TDS-2 has a corresponding eight-digit pulse accumulator. You can access these accumulators from the field programming terminal by entering the memory access code, @P01 & @P02, in response to the * prompt.

Example: Examine the pulse total for METER PORT 1.

| Transaction | Description |
| --- | --- |
| *@P01 | 5,607 pulses have received by the AC-4’s Meter Port 1 |

In similar fashion, you can enter @P02 to allow examination of pulse totals for Meter Port 2.   @P03 & @P04 accesses only the RF readings of RF ports 3, and 4.

### Changing Pulse Values

Manually changing the pulse total contained in a TDS-2 pulse accumulator involves entering the proper memory access code, @M01 & @M02 followed immediately by the desired new eight-digit pulse total. You must enter a full eight-digit number including any leading zeros.

Example 1 - Change Meter Port 2 pulse accumulator to 1234:

*@M0200001234 (Enter)

*

Example 2 - Clear Meter Port 1’s pulse accumulator to 0:

*@M0100000000 (Enter)

*

Teldata recommends that whenever you complete a change you examine the particular pulse accumulator to verify the result.

### Field Correlation of Pulse Totals to Meter Faceplate Reading

Correlation of TDS-2 accumulator pulse totals to a meter’s faceplate reading involves retrieval of the particular meter’s corresponding TDS-2 pulse accumulator pulse total and multiplying it by the pulse constant.

Example 1 - A single-phase electric meter is equipped with a Teldata Model RS-1 disk rotation sensor that produces one pulse for each complete rotation of the meter disk. The meter’s Kh is 7.2 watt-hours per disk rotation, which corresponds to 7.2 / 1,000 disk rotations = .0072 kWh per disk rotation. The pulse value for this installation is .0072 kWh per pulse.

| Transaction | Description |
| --- | --- |
| *@P01 (enter) | First access Meter Port 1/s pulse total: 00732485 |

*

Note: The @ symbol is an activation character only and does not display.

Now multiply this pulse total by the pulse value:

00732486 x .0072 = 5273.892KWH

the meter faceplate should read between 5273 and 5274.

Example 2 - The RS-1 equipped meter in the prior example has a faceplate reading of 00785. The installer wishes to set a pulse total corresponding to this faceplate reading into the TDS-2 Meter Port #2 pulse accumulator.

Step 1 Divide the meter’s faceplate reading by the pulse value to obtain the equivalent pulse total according to the formula on the next page.

PULSE VALUE = C/T*factor X Kh

PULSE RATE = X 1000

Therefore:

Faceplate reading / pulse value = pulse total

785 divided by .0072 = 109028 pulses

Step 2 Convert this pulse total to an eight-digit integer form and add leading zeros: pulse total = 00109028

| Transaction | Description |
| --- | --- |
| Step 3 | *@M0100109028 (Enter) Program TDS-2 Meter Port #1 pulse accumulator |

Step 4

*@M01 (Enter)	       Review programming

00109028		       Present reading

*

As a final check, multiply this pulse total by the pulse value to double check the entire process:	00109028 x .0072 = 785.0016

The faceplate reading of 785 is now verified.

### Using the Field Programmer to Verify  Readings

Obtaining a meter reading in the field is accomplished by entering Port Read Commands @P01 - @P04 at the * prompt. The interrogation can be performed on Meter Ports 1 through 4.  (Ports 3 and 4 are available with the RF interface only).  Regardless of the number of valid meter digits the a meter delivers, the reading returned will be eight digits with leading zeros.

NOTE: Encoder readings cannot be performed unless the TDS-2 has been properly configured. A separate port configuration register (@E11 & @E12) is provided for Meter Port 1 and 2. These registers are normally programmed by the TICOMM software in the Host computer during the first call in. See Appendix F for Port configuration.

Example - Read a five dial encoder connected to TDS-2 Meter Port 2:

*@P02 (enter)

00012345

*

Example – Read the full length of a data stream by bypassing the normal parsing performed by the TDS-4:

*@P02 (space) 99 (enter)

V;RB123456;IB02345915

*

# Replacing a TDS-2 in the Field

- Have the installed TDS-2 call the host computer.

- Using the Programming Terminal note the TIU ID, phone number, and accumulation registers:

- @M01, @M02

- Replace the TDS-2 but do not connect the telephone line

- Enter the same TIU ID, phone number, and accumulation register information into the memory of the new TIU using the @M01

- Verify the existing log memory of the unit is clear by entering the following commands:

- @C01<enter>

- @C02<enter>

- @C03<enter>

- @C04<enter>

- @CF<enter>

- Connect Phone line.

- Initiate a TDS-2 call to the host computer

# Power Fail Log and Alarm

Power Fail reporting by the TDS-2 is set with the E15 register. When this register is enabled and 12VAC is connected to the TDS-2 the unit will log power fails when they occur. The TDS-2 may also be configured to dynamically report power fails at the time of the outage. An alert call is initiated if the power fail time exceeds the preset time of the E15 register. If the power fail is less than the preset time the power fail will be logged and reported on the next scheduled call for the TDS-2.

| E15 = 00:00 | Power fail is disabled |
| --- | --- |
| E15 = 61:00 | Alert call is disabled all power fails will be logged. |
| E15 = 00:01 | Power Fail will be reported after one second and all power fails will be logged. |
| E15 =15:00 | All Power Fails will be logged and Power Fail Alert will be initialized if power fail time is longer then 15 minutes.. |

See Appendix G for additional information.

# Port Tampers

Port tampers are enabled in the E16 register.

Each hour the port status is checked and tampers are flagged. The register will make an alert call at the top of the hour upon sensing any new tamper conditions. Once a tamper has been reported, its continued presence will only be reported on regular call in schedules.

A 100,000 ohm resister must be placed across the wires connected to the G & D connectors of a meter so the TDS-2 can log and or dynamically report tampers.

Resister is located at the meter. See Appendix E.

E16 = 0000	All port tampers disabled

Second two digits are the tamper flag set by the TIU to indicate the active presence of a tamper on a port.

First two digits enable alert reporting of tampers. User settable.

See Appendix C for code matrix

NOTE: ABB/Kent encoders do not require the l00K resistor placement.

# Setting a delay before dialing

The E17 register allows the installer to program in a delay 	that allows the TDS-2 to wait, after detecting dial tone, before dialing.

The register accepts a two-digit entry with each increment up to 15 representing .5 seconds of delay.

Example:	@E17nn	(nn factory default = 00)

nn = 00	No delay & dial tone detect is disabled

nn = 01	0.5 seconds delay after dial tone is detected

nn = 15	7.5 seconds maximum delay

# Appendix A:

# Field Pro - Operations Manual
        TIU Programming Terminal

Function Keys

| F1 | Escape ESC - facilitates a quick return to the * prompt. |
| --- | --- |
| F2 | Back-space during an entry to correct a mistaken key stroke |
| CTRL +SHIFT+F1 | Change the data communications parameters. |
| F5 | Save the data communications parameters. |

Connection to the TIU

If possible, connection to the TIU programming port should be made before the terminal is turned on.

Connect the cable from the terminal to the ten pin port on the TIU labeled PROGRAM.

## Programming the TdS-2

- Type PRO

  - Example:

    - ID# =  (example)

    - GM1234ABC (enter)

    - HOST 1 PHONE # 18778418453

    - RING# = 25   (enter)

    - AUTO ANSWER = 0 (disabled)

- Shift@ C01 (enter) (wait approx. 6-8 seconds for exclamation

- Shift@ C02 (enter) point to signal command was executed.)

- Shift@ M0100000000 (enter)

- Shift@ M0200000000 (enter)

  - If using a Pulse Meter enter the face read as an 8 digit #          (face read= 12345, the M01 register would be entered as           M0100012345 = 8 digits. Encoder meters enter 8 zeros)

- Port Control String:

  - Shift@ E1144P1010 (enter) Port Control String for Port 1               Shift@ E12 (enter) Port Control for Port 2 = (if using P2)               (see back page for more port control strings)

- Shift@ P01 = Reads meter 1’s meter/pulse accumulation

- Shift@ P02 = Reads meter 2’s meter/pulse accumulation (if using P2)

- Shift@ E18-22 set to 01   example-E1801 (enter)

- Shift@ E2501 (enter)

- GO1 calls host and will allow the installers to verify communication with the host. CALL OK means only that the TIU has communicated with the host.

Error Messages

Error   = Line not available, line in use, line voltage is to low

Error1 = Host modem will not answer

Error2 = Host modem answers but fails in command sequence

Error5 = Call interrupted, customer off-hook

Notes = * is the starting point for all commands

@ is a command character and will not show on screen

Hook up phone line last thing before GO command

BEFORE LEAVING SITE, ALWAYS CHECK PORT1 (@PO1)

TO VERIFY COMMUNICATION BETWEEN MIU & METER

Encoded Port Control String

| Encoder Type | Control String | Read Parse | Hookup at TIU Port |
| --- | --- | --- | --- |
|  |  |  | C | G | D |
| Sensus / Rockwell 4 wheel | 2R402 | 2,4,6,8 | R | B | G |
| Sensus / Rockwell 6 wheel | 2V605 | 2,6,14,8 | R | B | G |
| Kent /ABB 6 wheel | 5K602 | 2,6,8,10 | G | B | R |
| Schlumberger 4 wheel (Neptune) | 3E402 | 1,8 | B | G | R |
| Schlumberger 6 wheel | 3F602 | 1,8 | B | G | R |
| Schlumberger 6 wheel Pro Read | 2R602 | 5,6,14,8 | B | G | R |
| Neptune 6 Wheel high resolution | 2R602 | 2,6,9,7 | B | G | R |

Pulse Meter Port Control Strings

| Pulse Meter Type | Control String | Read Parse | Hookup at TIU Port |
| --- | --- | --- | --- |
|  |  |  | C | G | D |
| Badger Read-o-matic w/o Remote display | P0099 | 1,8 |  | N | P |
| Kent RS Pulser | P0000 | 1,8 |  | N | P |
| Kent C700 Pulse Generator | P0099 | 1,8 |  | N | P |
| Sensus Pulse | P0099 | 1,8 |  | N | P |

Attachments

The charger connects to the side of the 9 pin adapter, located between the blue ribbon cable and the coiled modular cord.

Power Saver

The terminal will turn itself off if no characters are received and no keys are pressed for 10 minutes. The terminal can be restarted by pressing the ON/OFF button.

Battery

Operating time on a full charge is up to 48 hours of continuous use. To maximize the life of the NiCad battery pack the

# batteries should periodically be allowed to discharge completely. Charging the internal battery requires 16 hours of charging time if the battery is fully depleted. Re-charging must be done with the terminal turned off.

Appendix B: Factory Defaults

| Memory Register | Description | Factory Default |
| --- | --- | --- |
| @M01 | Pulse Accumulator for meter port 1 | 00000000 |
| @M02 | Pulse Accumulator for meter port 2 | 00000000 |
| @M21 | Power Fail Counter | 00000000 |
| @E00 | TIU ID | 0 |
| @E01 | Host 1 Phone Number | 00000000 |
| @E02 | Host 1 Call in Time Register | --/--/-- 00:00 |
| @E03 | Host 2 Phone Number | 00000000 |
| @E04 | Host 2 Call in Time Register | --/--/-- 00:00 |
| @E05 | Host 3 Phone Number | 00000000 |
| @E06 | Host 3 Call in Time Register | --/--/-- 00:00 |
| @E07 | Host 4 Phone Number | 00000000 |
| @E08 | Host 4 Call in Time Register | --/--/-- 00:00 |
| @E09 | Auto Answer Setting Register | 0 |
| @E10 | Number of rings required to alert | 10 |
| @E11 | Port Configuration Register for Port 1 | 10P0000 |
| @E12 | Port Configuration Register for Port 2 | 10P0000 |
| @E15 | Set Power Fail Log and Alert control | 00:00 |
| @E16 | Set Tamper function and Tamper Status | 00 |
| @E17 | Delay before dialing after dial tone detect | 00 |
| @E18 | Host to call for demand calls (00-15) | 01 |
| @E19 | Host to call for power fail (00-15) | 01 |
| @E20 | Host to call for manual call start (00-15) | 01 |
| @E21 | Host to call for Port 1 Tamper (00-15) | 01 |
| @E22 | Host to call for Port 2 Tamper (00-15) | 01 |
| @E25 | Dynamic off-hook detect set register | 01 |
| @E26 | Demand Window Settings Register | 00-00 |

# Appendix C: Tamper Register Matrix

| @E16nnnn |  |
| --- | --- |
| nn | First two digits enable call upon initial tamper logging to report tamper by TIU. |
| nn | Second two digits indicate presence of tamper condition on port. |

| User Settable | Display only set by TIU |
| --- | --- |
| 1st two digits | Call in at the top of the hour when tamper is sensed and logged. | 2nd two digits | Displays status of tamper port. |
| 00 | disable all ports | 00 | No Tamper |
| 01 | Port 1 | 01 | Port 1 Tamper |
| 02 | Port 2 | 02 | Port 2 Tamper |
| 03 | Port 1 & 2 | 03 | Port 1 & 2 Tamper |
| 04 | Port 3 | 04 | Port 3 Tamper |
| 05 | Port 1 & 3 | 05 | Port 1 & 3 Tamper |
| 06 | Port 2 & 3 | 06 | Port 2 & 3 Tamper |
| 07 | Port 1, 2 & 3 | 07 | Port 1, 2 & 3 Tamper |
| 08 | Port 4 | 08 | Port 4 Tamper |
| 09 | Port 1 & 4 | 09 | Port 1 & 4 Tamper |
| 10 | Port 2 & 4 | 10 | Port 2 & 4 Tamper |
| 11 | Port 1, 2 & 4 | 11 | Port 1, 2 & 4 Tamper |
| 12 | Port 3 & 4 | 12 | Port 3 & 4 Tamper |
| 13 | Port 1, 3 & 4 | 13 | Port 1, 3 & 4 Tamper |
| 14 | Port 2, 3 & 4 | 14 | Port 2, 3 & 4 Tamper |
| 15 | Port1, 2, 3 & 4 | 15 | Port 1, 2, 3 & 4 Tamper |

# Appendix D: Trouble Shooting

Problem			Suggested Course of Action

TDS-2 will not call-in	Check the voltage on the phone line - it 			must be 20 Volts or higher.

Check the phone number in the TDS-2

Using the butt set - call the host computer 			on the line.

Try another TDS-2 on the line.

TDS-2 keeps jumping off  	If you encounter repeated error code 5

the phone line during a    	(failed calls) when attempting to install

call-in.	a TDS-2. Verify whether another user is accessing the line locally by listening with a Butt Set.

Call the host computer operator and verify 			whether the TIU is being recognized 				properly by the system.

# Appendix E: Tamper Connection for Water Meter

# Appendix F: Port Configuration Registers

| Command | Description | Function |
| --- | --- | --- |
| @E11nnnnnnnn (Checksum value)(CR) | Set Port Configuration Register for TIU Port 1 | Data Stored |
| @E12nnnnnnnn (Checksum value)(CR) | Set Port Configuration Register for TIU Port 2 | Data Stored |
| Byte 1 value = 0-7 Byte 2 not used = 0 | Log length |
| TIU Data Logging Interval | Days before overwrite |
| 0 0 = Midnight only | 128 |
| 1 0 = once an hour | 149.3 |
| 2 0 = every 30 minutes | 74.6 |
| 3 0 = every 10 minutes | 24.8 |
| 4 0 = every 15 minutes | 37.3 |
| 5 0 = every 5 minutes | 12.4 |

NOTE:	5 and 10 minute logging intervals are software supported logging routines.  Please contacts FirstPoint to determine whether these log intervals are currently supported in your system.

Byte 3, 4, 5, 6 & 7 for Encoded Registers

|  | Byte 3 | Byte 4 | Byte 5 | Byte 6 & 7 |
| --- | --- | --- | --- | --- |
|  | Set Digit by Teldata. | Start Character in the datastream |  | Number of digits read including the start character (Byte 3) before the meter read begins |
| Encoded Registers Water Sensus 4 wheel encoded register Sensus 6 wheel encoded register Equimeter 4 wheel gas index Kent 6 wheel encoded register ARB 4 wheel encoded register ARB 6 wheel encoded register ARB 6 (Pro Read) Electric Landis & Gyr DEMS Teldata RF | 2 2 2 5 3 3 2 W | R V R K E F R n* | 4 6 4 6 4 6 6 n* | 02 05 02 02 02 02 02 nn* |

*n= any character may be used

Byte 3, 4, 5, 6 & 7 for Switch Closure/Pulse Registers

| Meters | Byte 3 | Byte 4 & 5 | Byte 6 & 7 |
| --- | --- | --- | --- |
| NOTE: This setting allows the TIU to filter out any pulses with a value greater than that set by bytes 6&7. | Teldata meter ID | Bytes 4 & 5 are not used in the TDS-2 | Length of time the pulse is in the Low State (switch in the on state). 2 numeric digits indicate the number of ticks. Each tick represents 10 milliseconds. For example: 02 = 20 milliseconds 04 = 40 milliseconds (00 = default to 20 ms) |
| Switch/Pulse Output Meters Teldata RS-1 Gas with Riotronics Sprague 400 Sprague S1A Rockwell 175 | P P P P P | 00 00 00 00 00 | 02 99 99 99 99 |

# Appendix G: Power Fail Programming Matrix

@E15 COMMANDS IS ADDED TO THE DC-4 SYSTEM

@E15MM:SS (CHECKSUM VALUE) (CR)

SET POWER FAIL TIME STAMPER LOG AND ALERT CONTROL REGISTER.

SS = MM = 00

BOTH POWER FAIL TIME STAMP LOG AND ALARM FUNCTION ARE DISABLED

SS = xx, MM > 60

POWER FAIL TIME STAMP LOG IS ENABLED AND POWER FAIL ALARM IS DISABLED

00<SS<60, 00<MM<60

POWER FAIL TIME STAMP LOG IS ENABLED AND AN ALARM CALL WILL BE INITIATED IF POWER INTERRUPTION TIME IS LONGER THAN THE TIME PERIOD SET BY MM: SS.

POWER FAIL CHECKING OCCURS AT THE TOP OF EVERY SECOND, THE CORRESPONDENT CALL REASON CODE IS 07.

THE MAXIMUM POWER FAIL TIME STAMP LOGS IS 64.

# Appendix H: Host to call matrix

Applies to registers E18 through E22.

(See Appendix B for factory defaults.)

| User Settable |
| --- |
| @Exxnn xx=register nn=host to call | Host to be called upon sensing event. |
| 00 | No host will be called |
| 01 | Host 1 |
| 02 | Host 2 |
| 03 | Host 1 & 2 |
| 04 | Host 3 |
| 05 | Host 1 & 3 |
| 06 | Host 2 & 3 |
| 07 | Host 1, 2 & 3 |
| 08 | Host 4 |
| 09 | Host 1 & 4 |
| 10 | Host 2 & 4 |
| 11 | Host 1, 2 & 4 |
| 12 | Host 3 & 4 |
| 13 | Host 1, 3 & 4 |
| 14 | Host 2, 3 & 4 |
| 15 | Host 1, 2, 3 & 4 |

# Appendix I: TIU Report Header

TIU Report Header Description

Use the @R command on the programming terminal and check the report header returned.

Data stream returned:	TLDTA02 DC2 iii...i  n1,n2,n3,n4,n5

TLDTA02 DC2 = Manufacturer and Device Type identifier

iii…i =  TIU ID (31character field)

n1 = 01 to 04 - Host   dialed

n2 = 01 to 99 - Reason for call code

01 normal scheduled call

03 Forced call by reason of start pins

04 Forced call by reason of GO command

05 On demand call by reason of Ring alert

06 On demand call by reason of Tone alert

07 Power Fail report

08 Tamper report

n3 = 01 to 99 - Call retry counter

n4 = 01 to 99 - Last failed call error code:

00 no error

01 no answer received from host

02 = TIU called computer; received carrier, but did not receive valid instructions from the computer within 30 seconds of the connection

03 not assigned

04 not assigned (noisy line condition in AC-4)

05 Communication attempt interrupted

06 Not assigned (break in carrier only for AC-4L)

n5 = 01 to 99 - Not assigned (00 at present)

# Glossary

AMR	Automatic Meter Reading - remote capture and transmission of consumption data.

Alert	A tone sent by the central computer over the telephone tone line. This tone is sent when the utility has called its customer and the customer or an answering machine has answered the call. If no one answers the phone the utility will ring the telephone line for the ring count and hang up. In either case the TIU will call the central computer.

ASCII	American Standard Code for Information Interchange - an industry standard for the binary encoding of characters.

baud	a measure of transmission speed over an analog telephoneline. TIUs transmit at 300 or 1200 baud.

index	the meter register on a gas meter

initial	The pulse count displayed on the face of a pulse generating count meter at the time the TIU is installed. The initial count is programmed into the TIU.

ITU-T	International Telecommunications Union, an international standards organization that focuses on common practices and policies in telecommunications. Previously known as CCITT.

Measured	Also known as usage sensitive pricing - a local service phone company method of pricing used to bill local phone calls. Measured service is often charged on the number of calls, the time of day, the distance traveled and the length of the call.

Meter 	A device attached to a utility meter that displays the current register read.

Meter Serial #	Usually an 8 digit number programmed into the meter register by the manufacturer and returned in the data stream from an encoded meter through the TIU to the software.

TIU	Telemetry Interface Unit - a component of an AMR system. The TIU reads consumption data from gas, water and electric meters installed at remote locations and transmits this data over the telephone line to the computer.

PB-01	Pulse Board Model 01. A PB-01 accepts pulse inputs from all types of utility meters with pulse output registers including pulse generators and dry or solid state switch closure. One or more PB-01s can be mounted on a Teldata Solutions TIU, Model IE-4.

port	A hardware location for passing data in and out of a computing device. TIUs have 6 ports - 4 for utility meters, 1 for the telephone line, and 1 for an ASCII terminal.

pulse dialing	Rotary style dialing as opposed to touch tone.

ring count	The number of telephone rings necessary to signal an TIU to call the central computer (1 to 99).

RS232C	An industry standard for serial communication connections.

serial port	A hardware location for sending and receiving serial data transmissions.

SQL	Structured Query Language (abbreviated SQL and commonly pronounced sequel) is the standard language for storing and manipulating data in relationship databases.

Touch tone	Keypad type dialing that sends DTMF tones over the telephone line. Tone dialing

# Advanced Programming:

## Clearing Logged Memory

The Logged memory for each port can be cleared by using the @C01-4 commands.  These commands are used to clear the memory of a unit that had previously been used.  If this command is not used the historic data from the previous installation will be uploaded to the host on the first call.

## Assigning Host To Call Vectors

The default setting for the E18 thru E22 registers is 01.  These 5 registers define which host is to be called when different call events are triggered.   The default vector 01, calls host one only.

See page 37 for the Host Vector table!

### Register	Register Defined

@E18		Sets the host or hosts to call for a Demand call

@E19		Sets the host or hosts to call for a Power-fail call

@E20		Sets the host or hosts to call for a Manual Call start

@E21		Sets the host or hosts to call for a Port 1 Tamper call-in

@E22		Sets the host or hosts to call for a Port 2 Tamper call-in

## Checking the Host To Call Vector Assignment

The host to call vector assignment can be checked with the hand programmer by entering the @E18 thru @E24 commands and pressing enter.  The TDS4 unit will respond with the 2-digit vector code.

## Changing Host To Call Vector Assignment

Changes to the vector assignments can be made with the hand programmer or other appropriate programming device.  Enter the register to be change followed by the 2-digit vector code and pressing enter.  It is a good practice to then check the register to make sure that the change was recorded.

Example:

@E2012 <enter>!  The exclamation mark is returned by the TDS4 indicating the command was valid and received

@E20 <enter>! 12 (check sum) indicates that the vector has been                              changed to 12

## Multi-Host Telephone Number Programming

If the Multi-Host feature of the system is to be used hosts 2-4 must be programmed into the TDS units by hand.  The register used to hold these numbers are E03, E05, and E07.  If Multi-Hosting is not used these registers must contain 8 Zero’s.  This is the factory default and prevents the unit from using these registers.  The pro command programs the host number one phone number and stores it in the E01 register.

To program these numbers, enter the telephone number the same as you would when using the PRO command, including any “P’s” and any access numbers if used.  The register entry can be up to 21 digits in length.

E03 is used to store the host 2s number, E05 stores host 3s number, and E07 stores host 4s number.

Example of entry: @E0313096922110 (enter)!

This programs the unit to have all host 2 calls to be placed to 13096922110

## Dynamic Off Hook Detection

The E25 register is used to set the operational characteristics for an off hook condition on the resident telephone line.  The default setting is E2501, this sets off hook detection to begin after dialing has been complete. The set-up used should be the characteristic that is least intrusive to the shared line but will still let the TDS to place its call.

The matrix for the E25 register is:

Code			Definition of the code

00                         Detection is disabled

01                         Detection is delayed until dialing is  complete(default)

02                         Detection is delayed 2seconds after dialing is complete

03                         Detection starts when answer tone is detected

04                         Detection starts when carrier is detected

An example entry for this command is: @E2501 (enter)!

# Warranty

FirstPoint Enegy Corporation warrants that all equipment sold pursuant to any resultant agreements shall be free from defects in material or workmanship at the time of delivery. Such warranty shall extend for one year. Buyer must provide notice to FirstPoint Energy Corp. within this prescribed warranty period of any defects: if the defect is not the result of improper usage, service, maintenance or installation and equipment has not been otherwise damaged or modified after delivery,FirstPoint Energy Corporation shall either replace or repair the defective part or parts of equipment or replace the equipment or refund the price at FirstPoint Energy Corporation’s option after return of such equipment by buyer to FirstPoint Energy Corporation

Shipment to FirstPoint Energy Corporation facility shall be borne on account of buyer, including all duties, fees, brokerage and special handling charges. Shipment from the FirstPoint Energy Corporation facility shall be borne by FirstPoint Energy Corporation.

Consequential Damages: FirstPoint Energy Corporation shall not be liable for any incidental or consequential damages incurred as a result of any defect in any equipment sold hereunder and FirstPoint Energy Corporation’s liability is specifically limited to its’ obligation described herein to repair or replace a defective part or parts covered by this warranty.

Exclusive warranty: The warranty set forth herein is the only warranty, oral or written made by FirstPoint Energy Corporation and is in lieu of and replaces all other warranties, expressed or implied, including the WARRANTY OF MERCHANTABILITY AND THE WARRANTY OF FITNESS FOR A PARTICULAR PURPOSE.

# Text boxes

TDS-2 Ground